Purpose / Objective

Guidance on the identification of hazards, assessment of risk and requirement for inspection, testing and tagging of electrical equipment.

Guidance to support decision making for electrical safety

This guide uses risk information and definitions from the Australian Standards AS/NZ 3760 and AS/NZ 3000 and is designed to assist in the decision making that will create safe work places efficiently. Manufacturers’ recommendations, plant and equipment risk assessments and other information should always be considered when making decisions on testing and tagging requirements.

Electrical appliances included in this guide are portable equipment, hand-held equipment (Table 1) and stationary equipment (Table 2), designed for connection to the low voltage supply by a supply cord, an appliance inlet or pins for insertion into a socket-outlet;

- Cord sets, cord extension sets and outlet devices (also known as electrical portable outlet devices (EPODs), or power boards);

- Flexible cords connected to fixed equipment in hostile environments;

- Portable power supplies (includes power adaptor/plug-pack, both of the safety isolating transformer and switch-mode type);

- Battery chargers including those for commercial or industrial use;

- Portable and transportable heavy duty tools such as high pressure washers and concrete grinders.

Hazards and risk factors for electrical equipment

The frequency of repetition of testing and tagging is determined by the equipment type and by examination of the environment in which the equipment is used or working. For indicative purposes a number of different environments are provided with recommended inspection/testing frequencies. These are based on the perception of the level of hazard and the degree of abuse to which the equipment is typically exposed.

The location is one in which the equipment or appliance is normally subject to events or operating conditions likely to result in damage to the equipment or a reduction in its expected life span. This includes, but is not limited to mechanical damage, exposure to moisture, heat, vibration, corrosive chemicals, sharp or heavy impact and dust.

New to Service

New electrical equipment that has never been put into use (i.e. other than second-hand equipment) does not have to be tested before first use. The date the electrical equipment was placed into service should be recorded on a fitted tag. Fitting a ‘new to service’ tag is an administrative task that can be carried out by the person purchasing or receiving the device.

NOTE: Medical and specialist laboratory equipment must have risk assessments based on manufacturers recommendations and have been purposely left out of this guide.

- Risk assessed testing and tagging requirement guide ‘Portable Equipment’

| Portable Items | Location | Movement | Other risk factors | Test & Tag Cycle |
| --- | --- | --- | --- | --- |
| Extension cords and power boards attached to stationary appliances or equipment | Office or other indoor space – no hostile environment factors | Rare, less than once per year | Cords not subject to flexing and pulling pressures, no impact risks | 5 years after initial visual inspection |
| Extension cords and power boards not constantly connected to stationary items | Available for use, not connected to stationary portable equipment | Variable | Cords constantly subject to flexing and pulling pressures, impact and other hostile environment elements are possible | Annual - plus constant inspection for visible damage |
| Desk top computer | Office used by staff – no hostile environment factors | Rare, less than once per year | Cords not subject to flexing and pulling pressures, no impact risks | 5 years after initial visual inspection |
| Desk top computer | Computer lab, shared space for student use | Rare, less than once per year | Cords not subject to flexing and pulling pressures, no impact risks | 5 years after initial visual inspection |
| Laptops, iPads and associated portable equipment chargers | Available for use, not connected to stationary portable equipment | Variable | Cords constantly subject to flexing and pulling pressures, impact risks are higher | Annual - plus constant inspection for visible damage |
| Toaster, kettle, sandwich press and microwave ovens | Kitchenette or office space | Often, switched on/off and possibly unplugged multiple times daily, heat and moisture present while in use | Cords subject to flexing, pulling and heat | Annual - plus constant inspection for visible damage |
| Portable fan heater | Office environment | Intermittently, used as required through one season then stored. In season it could be switched on and off daily | High risk item based on known incidents of fan heaters being damaged from storage and regular use | Annual - plus constant inspection for visible damage while in use |
| Portable air circulating fan (floor stand or desk stand) | Office environment | Intermittently, used as required through one season then stored. In season it could be switched on and off daily | High risk item based on known incidents of fan heaters being damaged from storage and regular use | Annual - plus constant inspection for visible damage while in use |
| Hand tools – construction (e.g drills, sanders etc) | Workshops and indoor / outdoor construction site | Often, switched on/off and possibly unplugged multiple times daily, | Cords subject to flexing, pulling and multiple ‘hostile environment’ elements | Annual (minimum may require more often) - plus constant inspection for visible damage |
| Hand tools – beauty (e.g. hair dryers, UV & LED lamps etc) | Shop or treatment rooms | Often, switched on/off and possibly unplugged multiple times daily | Cords subject to flexing, pulling and possible hostile environment elements | Annual - plus constant inspection for visible damage |
| Lighting, camera and other Arts equipment loaned to students | Unpredictable indoor / outdoor | Often, switched on/off and possibly unplugged multiple times daily | Cords subject to flexing, pulling and possible hostile environment elements | 6 monthly - plus inspection for visible damage every time it is hired out |

- Risk assessed testing and tagging requirement guide ‘Fixed or Stationary Equipment’

| Fixed or Stationary Appliances | Location | Movement | Other risk factors | Test & Tag Cycle |
| --- | --- | --- | --- | --- |
| Wall mounted hand drier | Toilet / bathroom foyer space, may be subjected to limited moisture | Never, rarely switched off at the wall and unplugged | Cords not subject to flexing and pulling pressures – no hostile environment | Not required |
| Wall mounted instant boiling water units | Kitchenette, may be subject to moisture, heat | Never, rarely switched off at the wall and unplugged | Cords not subject to flexing and pulling pressures – no hostile environment | Not required |
| Photocopier / printer (large floor standing machines) | Office or shared space – no hostile environment factors | Rare, less than once per year | Cords not subject to flexing and pulling pressures | Not required |
| Under sink hot water units | Kitchenette, may be subject to moisture, heat | Never, rarely switched off at the wall and unplugged | Cords not subject to flexing and pulling pressures – no hostile environment | Not required |
| Gas heaters | Indoor rooms, spaces | Never, rarely switched off at the wall and unplugged | Cords not subject to flexing and pulling pressures – no hostile environment | Not required |
| Water Coolers | Indoor rooms, spaces | Never, rarely switched off at the wall and unplugged | Cords not subject to flexing and pulling pressures – no hostile environment | Not required |
| Fixed equipment for construction (e.g. pedestal drills, pedestal grinders, lathes etc) | Workshops | Never, rarely switched off at the wall and unplugged | Subject to multiple ‘hostile environment’ elements | Annual (as a minimum, may be required more often in risk assessment) - plus constant inspection for visible damage |
| Refrigerator | Kitchenette or office space, laboratory | Rare, less than once per year | Cords not subject to flexing and pulling pressures, low impact risks but cold and damp risks | 5 years after initial visual inspection |
| Fixed in-service equipment/machinery | Workshops, laboratory, maintenance department | Never | Vary from equipment to equipment. Risk Assessment required. | Annually |
| Equipment for cleaning | Anywhere at VU | Often, switched on/off and possibly unplugged multiple times daily | Cords not subject to flexing and pulling pressures, low impact risks but cold and damp risks | Every 6 months |
| Hired equipment | Anywhere at VU | Depends upon usage | Vary from equipment to equipment. Risk Assessment required. | Prior to hire |
|  |  |  |  | 3 months |